## ELE
AREA | EQUIPMENT | ELECTRICAL CONSUPTION | [6 empty] | ELE. REAL
|  | KW | KVA | QTY | TOTAL (KVA) |  | % Potencia | % Tiempo | % Utilización | TOTAL (KVA)
LASER | METAL LASER 3000W GENERATOR + CHILLER | 23 | 28.75 | 4 | 115 |  | 33% | 60% | 19.8% | 22.77
| CHILLER FOR LASER | 5.0 | 6.25 | 4 | 25 |  | 50% | 50% | 25% | 6.25
| ELECTRICAL SPIKE SUPPRESSOR REGULATOR MODEL TOUCH 220VAC 100A | 0 | 0 | 4 | 0 |  | 0% | 0% | 0% | 0
| THREE-PHASE ELECTRIC POWER TRANSFORMER 60KVA-3F-220-380 | 0 | 0 | 4 | 0 |  | 0% | 0% | 0% | 0
| COMPRESSOR MODEL: BOSS DREI BCT-3022-SET SCREW COMPRESSOR, 30 HP/22 KW | 22 | 27.5 | 4 | 110 |  | 60% | 30% | 18% | 19.8
| DUST COLLECTOR FOR LASER CUTTING MACHINES | 0 | 0 | 4 | 0 |  | 0% | 0% | 0% | 0
| Sub-Total |  |  |  | 250 |  |  |  | 0% | 48.82
BENDING | BENDING MACHINE 200-TON WITH NC, 3.2 METERS INCLUDED ACCESSORIES 3 AXES + TOUCH PANEL (TP10S TOUCH) | 11.25 | 14.0625 | 1 | 14.0625 |  | 90% | 80% | 72% | 10.125
| SUPRESOR DE SOBRETENSIONES TRANSISTORIAS | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| ADDITIONAL CONTROL E300 | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| BENDING MACHINE 63-TON, NC, 1.6 METERS, AND ACCESSORIES INCLUDED. 3-AXIS + TOUCH PANEL (TP10S TOUCH) | 5.5 | 6.875 | 1 | 6.875 |  | 100% | 80% | 80% | 5.5
| STAMPING PRESS 40 TON | 3 | 3.75 | 1 | 3.75 |  | 100% | 80% | 80% | 3
| SUPRESOR DE SOBRETENSIONES TRANSISTORIAS | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| Sub-Total |  |  |  | 24.6875 |  |  |  | 0% | 18.625
DEBURING | DEBURING MACHINE BIG SIZE XRB SAND-P1300 | 54 | 67.5 | 1 | 54 |  | 35% | 80% | 28% | 15.12
| DEBURING MACHINE SMALL SIZE XRB Open Table SAND-R330 | 7.5 | 9.375 | 1 | 7.5 |  | 35% | 80% | 28% | 2.1
| WATER SandBlasting SAND-U520 de 200L | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| TABLES & TOOLS FOR GRINDING | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
|  |  | 0 | [5 empty] | 0% | 0
| Sub-Total |  |  |  | 61.5 |  |  |  | 0% | 17.22
COATING | ELECTROSTATIC PAINTING CABINET, AREA 3.90 X 2.40 MTS | 5 | 6.25 | 1 | 6.25 |  | 100% | 100% | 100% | 6.25
| OVEN: POWDER COATING OVEN, 4000 X 3000 MM AREA, 380V ELECTROSTATIC | 10 | 12.5 | 1 | 12.5 |  | 100% | 100% | 100% | 12.5
| SPRAY GUN AND MACHINE FOR PAINT APPLICATION, ELECTROSTATIC AREA FEM1910S FULL SET | 1 | 1.25 | 1 | 1.25 |  | 100% | 100% | 100% | 1.25
|  |  | 0 |  | 0 |  |  |  | 0% | 0
|  |  | 0 |  | 0 |  |  |  | 0% | 0
| Sub-Total |  |  |  | 20 |  |  |  | 0% | 20
WELDING | LASER WELDER: 2000-W CAPACITY, 3-IN-1 MULTIFUNCTION WITH AUTOMATIC FEEDER AND ACCESSORY SET. VOLTAGE REGULATOR INCLUDED. | 2 | 2.5 | 1 | 2.5 |  | 80% | 50% | 40% | 1
| THREE-PHASE ELECTRIC POWER TRANSFORMER 50KVA-3F-220-380 | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| Sub-Total |  |  |  | 2.5 |  |  |  | 0% | 1
TOOLING | BENDING TOOLINGE SET | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| PRODUCTION CARS FOR TOOLING | 0 | 0 | 2 | 0 |  |  |  | 0% | 0
| PAINT HANGERS & CARRIERS | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| PRESS MACHINE 65T | 10 | 12.5 | 1 | 12.5 |  | 100% | 80% | 80% | 10
| TOOLING MFG LOCAL | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| Sub-Total |  |  |  | 12.5 |  |  |  | 0% | 10
ERECTION | FACILITIES INSTALLATION | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| SUB-ESTACION 250 - 300 KVA | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| ELECTRICAL FEEDERS | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
|  |  | 0 |  | 0 |  |  |  | 0% | 0
|  |  | 0 |  | 0 |  |  |  | 0% | 0
| Sub-Total |  |  |  | 0 |  |  |  | 0% | 0
AUX. EQUIPMENTS & CONTRACTS | 7-TON TRUCK, BRAND: ELAM FAW | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| FORKLIFT 3000 kg | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| TRUCK PLATFORM | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| NITROGEN GAS TANKS | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| PUNCHING AND MODIFICATION | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| MANUFACTURE OF 2 WASHING TABLES | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| 10,000-LITER WATER TANK | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| PRESSURE WASHER | 0.5 | 0.625 | 1 | 0.625 |  | 100% | 100% | 100% | 0.625
| STATIONARY TANK | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| ENGINEERING DEPARTMENT COMPUTERS | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| SOFTWARE | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| TRAINING | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| LP GAS | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| NITROGEN RENTAL laserkid | 2 | 2.5 | 1 | 2.5 |  | 100% | 100% | 100% | 2.5
| INTERNET AND NETWORK | 2 | 2.5 | 1 | 2.5 |  | 100% | 100% | 100% | 2.5
| OTHERS | 0 | 0 | 1 | 0 |  |  |  | 0% | 0
| Sub-Total |  |  |  | 5.625 |  |  |  |  | 5.625
| TOTAL |  |  |  | 376.8125 | KVA |  |  |  | 121.29 | KVA
|  |  |  | Objetivo..!!! | 250 | KVA |  |  |  | 250 | KVA
Note on J2: Precision: Utilización se considera con 2 Factores Potencia y Tiempo de Uso de Maquina si no en Consumo Real Ya que el Acero se corta con una capacidad menor en el Laser. 1200W a 1500W
Note on B14: Precision: TROQUELADORA DE 30 A 35 TON

## Deburring
7.5 | 2 | 15
5.5 | 1 | 5.5
1.5 | 1 | 1.5
22

## cirotec2024
No. | Descripción detallada ó de catálogo | Area | Potencia (KW) | Potencia (HP) | Voltaje (V) | Corriente (A) | Verificación (A) | Phases (#) | Tierra (Ohms) | Neutro
1 | Maquina de soldar (Soldadura electrodo) lincon electric | Weld | 24.2 | 32.45 | 220/440 | 110/55 |  | 3
2 | Máquina para soldar con microalambre | Weld | 10.5 | 14.08 | 220 | 48 |  | 2
3 | Maquina de soldar Fronius | Weld | 13.86 | 18.6 | 220/440 | 63/35 |  | 3
4 | Soldadura Argón Miller | Weld | 6.6 | 8.8 | 220 | 30 |  | 2
5 | Punteadora mecanica | Weld | 20 | 26.8 | 220 | 70 | 72 | 2
6 | Cortadora de metales urrea | Weld | 3 | 4 | 220 | 13.64 | 10.2 | 3
7 | Cortadora makita | Weld | 1.73 | 2.31 | 115 | 15 | 13.1 | 1
8 | Compresor de aire presión 175 Llb/plg | Weld | 3.7 | 4.9 | 220 v | 12.5 | 11.5 | 3
10 | Lasér CNC de fibra Óptica X0 | Steel | 12 | 30.8 | 220 | 60.6 | 14.1 | 3 | SI
11 | Chiller | Steel | 5.0 | 6.7 | 220 | 21.5 | 24 | 2
12 | Lasér CNC de fibra Óptica X3 | Steel | 14.4 | 19.3 | 380 | 38 | 21.4 | 3
13 | Chiller X3 | Steel | 5.06 | 6.7 | 380 | 13.3 | 6.7 | 3
14 | Compresor BCT-3020-Set | Steel | 22 | 29.49 | 380 | 28 | 34 | 3 |  | 127
14.1 | Secador de compresor BCT-3020-Set | Steel | 0.765 | 0.001 | 220 | 3.3 | 3.3 | 2 | SI
15 | Compresor BC-T2015 | Steel | 15 | 20.1 | 220 | 68.2 | 34 | 3
16 | Compresor de aire presión 175 Llb/plg | Steel | 3.7 | 4.9 | 220 v | 12.5 | 11.3 | 3
17 | Compresor I 800 | Steel | 7.46 | 10 | 220 | 24.8 | 21.2 | 3 | SI
19 | Lasér CNC de fibra Óptica Jet 3015 | Steel | 23 | 30.8 | 380 | 60.6 | 12.2 | 3 | SI
20 | Chiller para Jet 3015 | Steel | 5 | 6.7 | 220 | 16.8 | 15.7 | 2 | SI
21 | Lasér CNC de fibra Óptica FC315A | Steel | 23 | 30.8 | 380 | 60.6 | 13 | 3
22 | Chiller para FC315A | Steel | 5.5 | 6.7 | 380 | 13.4 | 11.9 | 3 | SI
23 | Dobladora FlexCNC 63 TON | Doblado | 5.5 | 7.3 | 220 | 20.5 | 10.1 | 3 |  | 124.2
24 | Dobladora FlexCNC 125 TON | Doblado | 7.5 | 10 | 220 | 27 | 11.7 | 3 |  | 124.2
25 | Prensa | Doblado | 3.730 | 5 | 230 | 13 | 21 | 3 |  | 124.2
26 | Troqueladora Convencional | Doblado | 2.2 | 2.9 | 220 | 20 | 6.9 | 3
27 | Sierra cinta Vertical | Maquinado | 1.5 | 2 HP | 220 | 6.78 | 3.1 | 3
28 | Sierra cinta horizontal | Maquinado | 2.2 | 2.9 | 220 | 8.22 | 5.7 | 3
29 | Compresor de aire presión 175 Llb/plg | Maquinado | 3.7 | 4.9 | 220 v | 12.5 | 19 | 3
30 | Afiladora | Maquinado | 0.18 | 0.2 | 220 | 0.8 | 0.8 | 3
31 | Router CNC | Maquinado | 8.5 | 6 | 220 | 43 |  | 2
32 | Centro de maquinado CNC | Maquinado | 9.6 | 12.8 | 220 | 30 | 8.7 | 3
33 | Fresadora lector digital (MH-01-FLD02) | Maquinado | 2.24 | 3 | 220 | 10.17 | 5.7 | 3 |  | 0
34 | Fresadora lector digital (MH-01-FLD03) | Maquinado | 2.24 | 3 | 220 | 10.7 | 3.7 | 3
35 | Fresadora lector digital (MH-01-FLD01 | Maquinado | 2.24 | 3 | 220 | 10.7 | 4.2 | 3
36 | Fresadora lector digital (MH-01-FLD04) | Maquinado | 2.24 | 3 | 220 | 10.7 | 5.6 | 3
37 | Fresadora CNC (MH-01-FCNC02) | Maquinado | 3.7 | 5 | 220 | 15 | 5.6 | 3 |  | 127.1
38 | Fresadora CNC (MH-01-FCNC03) | Maquinado | 3.7 | 5 | 220 | 14.3 | 3.8 | 3 |  | 127.2
39 | Torno CNC | Maquinado | 15 | 20.1 | 220 | 41 | 7.2 | 3 | SI
40 | Rectificadora de superficies planas | Maquinado | 6.4 | 8.5 | 220 | 40 | 10 | 3 |  | 127.1
41 | Torno engranado | Maquinado | 7.5 | 10 | 220 | 26.6 | 19.2 | 3
42 | Torno Saturno (MH-01-TE01) | Maquinado | 1.5 | 2 HP | 220 | 6.09 | 4.1 | 3 |  | 127.5
43 | Esmeril | Maquinado | 0.56 | 3/4 HP | 127 | 4.4 | 3.8 | 1
44 | Tómbola | Maquinado | 0.2 | 1/2 HP | 208-230 | 1.8 | 1.6 | 3
45 | Horno de templado | Maquinado | 1.4 | 1.8 | 115 | 12 |  | 1
46 | Lijadora | Maquinado | 1.5 | 2 | 220 | 6.32 |  | 2
47 | Esmeril | Maquinado |  |  | 220 |  | 13 | 3